## Building Energy Loss
Energy loss of a building
| V,air,in |  |  |  |  | V,air,out | at 20°C
at 0°C
Qout = Qenvelope+Qair
Energy Balance
Qout = Qin
Qin
Power = Energy / Time |  |  |  |  | Energy Unit: JOULE (J)
Unit of Power = WATT (W) |  |  |  |  | Power unit: J/s (WATT, W)
Tin = | 20 | °C | 293 | K | 1 kilowatt-hour (kWh) = 3.600.000 J
Tout = | 0 | °C | 273 | K
Delta T = | 20 | °C | 20 | K
.
.

## Envelope loss Single layer
Envelope loss |  | Single layer
|  | concrete wall |  | tickness t = | 0.25 | m
|  |  |  | Tout (°C) = | 0
Tin (°C) = | 20 |  |  | Qout = ? |  | W
|  |  |  | S = | 30 | m2
|  |  |  | t = | 0.25 | m
| Twin |  | Twout
Thermal resistances
| Qout |  |  | Ohm's law
|  |  |  | Q = (T1-T2)/Rtot = |  | 1411.7647 | W
| hin |  | hout
|  |  |  | T1 |  | T2
Q
|  | lambda | (thermal conducibility of the wall) |  |  | 1 | W/mK
Internal convection |  | conduction | external convection
| R1 | R2 | R3
Thermal resistances in series
hin = | 8 | W/m2K | R1 = | 1/(S*hin) = |  | 0.0041667 | K/W
lambda = | 1 | W/mK | R2 = | t/(S*lambda) = |  | 0.0083333 | K/W
hout = | 20 | W/m2K | R3 = | 1/(S*hout) = |  | 0.0016667 | K/W
|  |  | Rtot = | R1+R2+R3 = |  | 0.014167 | K/W
Now we write the Ohm's law just for R1
Q = (Tin-Twin)/R1 |  | Twin = Tin - Q*R1 = |  | 14.1176 | °C
Now we write the Ohm's law just for R2
Q = (Twin-Twout)/R2 |  | Twout = Twin - Q*R2 = |  | 2.3529 | °C
x (m) | T (°C)
0 | 20 | Tin
1 | 14.1176 | Twin
1.25 | 2.3529 | Twout
2.25 | 0 | Tout

## Envelope loss multipl layers
Envelope loss |  | Multiple layers
|  | concrete wall |  |  | tickness t = | 0.25 | m
[5 empty] | Tout (°C) = | 0
Tin (°C) = | 20 |  |  |  | Qout = ? |  | W
[5 empty] | S = | 30 | m2
[5 empty] | t1 = | 0.02 | m
| Twin |  |  | Twout | t2 = | 0.25 | m
[5 empty] | t3 = | 0.14 | m
Thermal resistances
| Qout |  |  |  | Ohm's law
[5 empty] | Q = (T1-T2)/Rtot = |  | 135.5932 | W
| hin |  |  | hout
[5 empty] | T1 |  | T2
Q
Transmittance formula: Q=(T1-T2)*U*S
[5 empty] | Transmittance U = Q/(S*(T1-T2)) = 1/(S*Rtot) = |  |  |  | 0.22599 | W/m2K
Rtot = 1/(U*S) => U = 1/(S*R)
|  | lambda |  | (thermal conducibility of the wall) |  |  | 1 | W/mK
Internal convection |  | conduction |  | external convection
| R1 | R2 | R3 | R4 | R5
Thermal resistances in series
hin = | 8 | W/m2K |  | R1 = | 1/(S*hin) = |  | 0.0041667 | K/W
lambda1 = | 1 | W/mK |  | R2 = | t1/(S*lambda1) = |  | 0.0083333 | K/W
lambda2= | 0.5 | W/mK |  | R3 = | t2/(S*lambda2) = |  | 0.016667 | K/W
lambda3 = | 0.04 | W/mK |  | R4 = | t3/(S*lambda3) = |  | 0.11667 | K/W
hout = | 20 | W/m2K |  | R5 = | 1/(S*hout) = |  | 0.0016667 | K/W
|  |  |  | Rtot = | R1+R2+R3 = |  | 0.1475 | K/W
Now we write the Ohm's law just for R1
Q = (Tin-Twin)/R1 |  | Twin = Tin - Q*R1 = |  |  | 19.435 | °C
Now we write the Ohm's law just for R2
Q = (Twin-Twout)/R2 |  | Twout = Twin - Q*R2 = |  |  | 18.3051 | °C
x (m) | T (°C)
0 | 20 | Tin
1 | 19.435 | Twin
1.25 | 18.3051 | Twout
2.25 | 0 | Tout

## Air loss
Air loss
Typical ventilation factors
[6 empty] | residential |  | 0.5 V/h
[6 empty] | commercial |  | 1 V/h
[6 empty] | schools |  | 2 V/h
Vdot |  |  |  | Vdot |  | V = | 100 | m3
0 °C |  |  |  | 20 °C |  | Vdot = | 0.013889 | m3/s
Mdot |  |  |  | Mdot |  | rho = | 1.2 | kg/m3
[6 empty] | Mdot =Vdot*rho = |  | 0.016667 | kg/s
Force is measured in Newton (N)
Mass is measured in kilograms (kg)
VMC machines |  | Controlled Mechanical Ventilation
| 20°C |  |  | 5 °C
75% of heat is recovered
| 15°C |  |  | 0 °C
|  |  | Without VMC |  | With VMC
Qvent = Mdot*cp*(Tin-Tout) = |  |  | 333.3333 | W | 83.3333 | W | 250 | W recovered
Specific Entalpy E = cp*T |  |  | J/kg |  |  |  | 15 | W used
Specific Thermal Capacitance at constant pressure = |  |  |  |  | 1000 | J/kgK | 16.6667 | COP